22 11 16 DOMESTIC WATER PIPING

PART 1 – GENERAL

  - SUMMARY

- This Section specifies the water distribution piping system, including potable cold, hot and re-circulated hot water piping including associated fittings, and specialties within the building.

  - RELATED SECTIONS

- Drawings and general provisions of the Contract, including General and Supplementary Conditions, Section XXXXXX and Division 1 Specification sections apply to work of this section.

  - REFERENCE DOCUMENTS

- ASTM F 2389-16 - Standard Specification for Pressure-rated Polypropylene (PP) Piping Systems

- CSA B137.11 - Polypropylene (PP-R) Pipe and Fittings for Pressure Applications

- NSF/ANSI 14 – Plastic Piping System Components and Related Materials

- NSF/ANSI 61 – Drinking Water Systems Components – Health Effects

- DIN-DVS 2207-11 2017 – Welding thermoplastic materials – Heated element welding of pipes, piping parts and panels made of polypropylene

  - DEFINITIONS

- Definitions shall be in accordance with local plumbing codes and ASTM F 2389.

  - ACTION SUBMITTALS

- Material submittal booklet naming each product to be used identified by manufacturer and product number, in accordance with Section XXXXXX.

- System purging and disinfecting activities report

- Field quality control reports

- Warranty information

  - QUALITY ASSURANCE

- Material shall be certified by NSF International as complying with NSF 14, NSF 61, and ASTM F 2389 or CSA B137.11.

- Material shall comply with manufacturers specifications.

- Special Engineered products shall be certified by NSF International as complying with NSF 14.

  - PERFORMANCE REQUIREMENTS

A. Provide components and installation capable of producing hydronic piping systems with the following working-pressure ratings:

1. Hot-Water Piping: XXX psig at XXX deg. F

2. Hot-Water Return Piping: XXX psig at XXX deg. F

  - FIELD CONDITIONS

- Interruption of Existing Water Service: Do not interrupt water service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary water service in accordance with requirements indicated:

- Notify [Architect] [Construction Manager] [Owner] no fewer than [two] <Insert number> days in advance of proposed interruption of water service.

- Do not interrupt water service without [Architect's] [Construction Manager's] [Owner's] written permission.

  - DELIVERY, STORAGE AND HANDLING

- Inspect the pipe upon receipt to ensure that it has not been damaged during shipping.

- Damaged pipe should be cataloged and returned for replacement following distributor’s procedures for returns.

- Protect piping, valves, fittings, etc. before installation in accordance with manufacturer’s written instructions.

- Always store the pipe on a flat surface. When storing the pipe on racks or supports on the ground always have at least four supports, evenly spaced, under a 19-ft length. Place plywood on top of the supports to prevent warping.

- Piping shall be shipped from the factory with capped ends and stored on supports off the ground with ends covered at all times to prevent nesting of insects, birds, and other animals. Any pipe found to be without end-caps or not raised off of the ground should be cleaned by the contractor prior to installation.

- Protect piping from accumulation of dirt and debris in and around piping/components.

- If the pipe is removed from its bag, or the bag has been damaged do not store the pipe unprotected from UV rays (sunlight) for longer than six months. Pipe that is exposed to direct sunlight for longer than six months will not be covered under the warranty.

- Never place the forks of a forklift into the ends of the pipe. The interior of the pipe may be damaged and can cause it to crack. Handlers may use a padded rug ram inside the pipe or use a crane or lift to handle larger pipe.

- In cold weather, take extra care when handling the pipe. Cold temperatures reduce the pipe’s flexibility, making it more susceptible to impact damage.

1.10     PRECONSTRUCTION MEETING

A. Preconstruction Testing Service: [Owner will engage] [Engage] a qualified testing agency to perform preconstruction testing on water quality.

PART 2 – PRODUCTS

2.01 	PIPE AND PIPING PRODUCTS

A. 	Pipe shall be manufactured from a PP-R resin (Fusiolen) meeting the short-term properties and long-term strength requirements of ASTM F 2389.  The pipe shall contain no rework or recycled materials except that generated in the manufacturer's own plant from resin of the same specification from the same raw material.  All pipe shall be made in an extrusion process.  Domestic hot water shall contain a fiber layer (faser) to restrict thermal expansion. All pipe shall comply with the rated pressure requirements of ASTM F 2389.  All pipe shall be certified by NSF International as complying with NSF 14, NSF 61, and ASTM F 2389 or CSA B137.11.

B. 	Pipe shall be Aquatherm® Green Pipe®, or Green Pipe® MF (Faser®), available from Aquatherm, NA.  Piping specifications and ordering information are available at www.aquatherm.com.

2.02 	FITTINGS

A.	Fittings shall be manufactured from a PP-R resin (Fusiolen) meeting the short-term properties and long-term strength requirements of ASTM F 2389.  The fittings shall contain no rework or recycled materials except that generated in the manufacturer's own plant from resin of the same specification from the same raw material.  All fittings shall be certified by NSF International as complying with NSF 14, NSF 61, and ASTM F 2389 or CSA B137.11.

- Fittings shall be Aquatherm® Green pipe® available from Aquatherm, NA.  Fittings specifications and ordering information are available at www.aquatherm.com.

- Pipe shall not be threaded. Threaded transition fittings per ASTM F2389 shall be used where a threaded connection is required.

- Fittings shall be installed according to the manufacturer’s instructions.

2.03      WARRANTY

A. Manufacturer shall warrant pipe and fittings for 10 years to be free of defects in materials or manufacturing.

- Warranty shall cover labor and material costs of repairing and/or replacing defective materials and repairing any incidental damage caused by failure of the piping system due to defects in materials or manufacturing.

- Warranty shall be in effect only upon submission by the contractor to the manufacturer of valid pressure/leak test documentation indicating that the system was tested and passed the manufacturer’s pressure/leak test.

- Installers shall be trained and certified to install the pipe according to the manufacturer’s guidelines. Contact your local Aquatherm representative for training.

E.  Warranty shall be extended to prefabricated parts constructed by the manufacturer.

2.04	SMOKE AND FIRE RATINGS

A.  Where indicated on the drawings that a Plenum-rated Piping System is needed, then the pipe shall be wrapped and/or insulated with standard fiberglass or mineral wool pipe insulation, field installed.

- For domestic hot water or heating water systems, fittings may be left bare, no closer than every 6 ft. of pipe.

- For domestic cold water or chilled water systems the entire piping system must be wrapped or insulated to prevent condensation.

- The pipe, wrap or insulation as a system shall meet the requirements of CAN/ULC-S102.2-03, ASTM E84 or UL 2846.

- The system shall have a Flame Spread Classification of less than 25 and Smoke Development rating of less than 50.

2.05 	UV PROTECTION

A.  Where indicated on the drawings that the pipe will be exposed to direct UV light for more than 30 days, it shall be provided with a Factory applied, UV-resistant coating or alternative UV protection.

- Note that moulded fittings ½” – 4” do not need to have UV protection. Larger moulded fittings (6”-10”) and segmented fittings will need to be protected from UV.

2.06      THERMAL AND VAPOR BARRIER

- Insulation materials furnished and installed hereunder should meet the minimum thickness requirements of American Society of Heating, Refrigeration, and Air Conditioning Engineers ASHRAE 90.1 (current edition), "Energy Efficient Design of New Buildings."  However, if other factors such as condensation control or personnel protection are to be considered, the selection of the thickness of insulation should satisfy the controlling factor.

- Where standard pipe insulation is indicated on the drawings or in these specifications, the contractor shall provide a thermal (radiant, conductive, and convective) and vapor barrier insulation. The insulation products shall be provided in ______ R-value and _____thickness or as indicated on the drawings or elsewhere in these specifications. The standard pipe insulation shall be UV resistant, mold growth resistant and not contain asbestos, lead, mercury, or mercury compounds.

- For indoor systems operating at temperatures from 0°F (-18°C) to 200°F (93°C) and pipe sizes from ½” (20mm) to 12” (315 mm):

- Owens Corning TM Fiberglas TM Insulation for Aquatherm with ASJ Max® Positive Closure System, or approved equal.

- For systems operating below ambient (32°F (0°C) to +65°F (18°C)) temperature and pipe sizes from ½” (20mm) to 12” (315 mm):

- Owens Corning TM Vapor Wick® Pipe Insulation for Aquatherm, or approved equal.

- Other approved manufacturers include:

- Owens Corning

- Johns Manville

- National Rockwool

- Approved Equal

  - INTEGRATION OF AQUATHERM PIPE WITH OTHER SYSTEMS

- General

- When integrating Aquatherm piping systems with other systems or components not made of PP-R (e.g. components not made of PP-R like valves, pumps, other piping, check valves, strainers, etc.), take care to ensure the operating parameters for PP-R will not damage other materials in the system or vice versa.

- Verify all parts of the system as compatible with the medium being carried before installation. Aquatherm pipe does not require treatment to protect it from corrosion. Metals (ferrous and non-ferrous) in the system may be susceptible to corrosion. Provide water treatment to protect system metals.

- Do not mix Aquatherm pipe with other piping systems in conditions that will cause the other system or components to fail.

- The issues described here are only of concern in DHWR-systems. For domestic cold water (DCW) and mechanical (heating-cooling)-systems no additional requirements or actions are necessary.

- Domestic Hot Water Recirculation Systems (DHWR)

- When there is copper piping used in conjunction with PP-R in a DHWR system, take care to ensure the operating conditions will not cause degradation or erosion/corrosion of the copper.

- Follow the Copper Development Association guidelines (CDA Publication A4015-14/16: The Copper Tube handbook – www.copper.org) for sizing, temperature and flow velocity in the copper tubing.

- Sustained high levels of copper in DHWR piping can damage components within the system, even PP-R.

- Damage caused by copper in the water resulting from erosion/corrosion or other degradation of copper components in the DHWR system will void the Aquatherm warranty.

- It is considered good design and operational practice to ensure that the maximum HW-temperature within any part of the system / loop does not exceed 140°F (60°C). Some regulations and codes further restrict the temperature at any fixture to a maximum of 120°F (50°C).

- Importantly, the maximum temperature used must not exceed the rating of the pipe for the operating pressure. (See Aquatherm Design Guide table: “Systems with Constant Operating Parameters”.

- Flow rates in a DHWR system should not exceed 1.5 ft./sec (0.5 m/s) anywhere in the system, except in some special cases where velocities up to 3 ft./sec (1 m/s) are needed to achieve proper flow temperature. The CDA Publication A4015-14/20 - The Copper Tube handbook - limits the velocity in DHWR system to similar rates.

- When re-piping an existing DHWR-system originally installed in copper tubing, ensure all possible copper is replaced. If some copper remains as part of the system, strictly follow the rules and guidelines of the Copper Development Association (CDA Publication A4015-14/20: The Copper Tube Handbook) regarding flow rates and water conditions.

- Small amounts of copper or brass in valves and other equipment will generally not cause an issue. If the copper fails, it may degrade O-rings, gaskets, PP-R and other components as well, shortening their service life.

- When adding PP-R to an existing copper system in a DHWR-application, the level of copper in the water shall be tested. These levels shall not exceed 0.1 mg/L (ppm).  Higher levels of total copper indicate that the copper pipe is corroding /eroding due to system and/or water conditions. See section 2.08.B.4 above. Do not install PP-R in the system under these conditions.

- DHWR system shall be Hydraulically balanced.

- Hydraulic-balancing-valves shall be installed in every circulating loop throughout the complete system to ensure the required flow rate is maintained for each area of the building and ensure that proper flow velocity of the smaller return piping is maintained at or below the manufacturer’s or CDA’s recommendations.

- Pipes shall be sized to avoid water hammer and excessive surge pressures. Pump systems operating with on/off cycling, or pumps over-sized for the piping, can create high pressure and fatigue the piping material.

- Avoid cavitation which can lead to excessive system noise and, more importantly, can result in the erosion and degradation of the pipe surface and other components.

- Properly sized variable-speed (VFD) constant pressure pumping systems and pressure-sustaining valves can alleviate cavitation and water hammer.

- The pumps shall be sized to operate at maximum efficiency with the lowest energy usage for the required flow rate.

- Install thermostats in hot-water circulation piping. Comply with requirements for thermostats in Section 221123 "Domestic Water Pumps."

- Install thermometers on [inlet and] outlet piping from each water heater. Comply with requirements for thermometers in Section 220519 "Meters and Gages for Plumbing Piping."

PART 3 - EXECUTION

- EARTHWORK

  - Comply with requirements in Section 312000 "Earth Moving" for excavating, trenching, and backfilling.

- PIPING INSTALLATION

  - Drawing plans, schematics, and diagrams indicate general location and arrangement of domestic water piping.  Indicated locations and arrangements are used to size pipe and calculate friction loss, expansion, and other design considerations.  Install piping as indicated unless deviations to layout are approved on coordination drawings.

  - Installers shall be trained and certified to install the pipe according to the manufacturer’s guidelines. Contact your local Aquatherm representative for training.

  - Install listed pipe materials and joining methods below in the following applications:

    - Underground Piping: Polypropylene (PP-R) piping in SDR 7.4 or 11 per manufacturer’s instructions and ASTM D2774.

    - Aboveground:  Polypropylene (PP-R) piping in SDR 7.4 or 11 based on the required minimum pressure rating and use temperature, in accordance with manufacturer’s instructions and ASTM F2389.

  - Installation must be accomplished with the proper tools for installing Aquatherm piping following manufacturer’s instructions. Installation tools are available from your local Aquatherm representative. Tools may be purchased or rented.

  - Install domestic water piping level and plumb.

  - Install piping indicated to be exposed and piping in equipment rooms and service areas at right angles or parallel to building walls.  Diagonal runs are prohibited unless specifically indicated otherwise.

  - Install piping free of sags and bends.

  - Install piping to permit valve servicing.

  - Install piping above accessible ceilings to allow sufficient space for ceiling panel removal, and coordinate with other services occupying that space.

  - Flanges and unions may be used for aboveground piping joints unless otherwise indicated. Do not use flanges and unions in direct bury applications.

- FUSION WELDING OF JOINTS

  - Install fittings and joints using socket-fusion, elecrofusion, or butt-fusion as applicable for the fitting type.  All fusion-weld joints shall be made in accordance with the pipe and fitting manufacturer’s specifications and product standards.

  - Fusion-weld tooling, welding machines, and electrofusion devices shall be as specified by the pipe and fittings manufacturer.

  - Prior to joining, the pipe and fittings shall be prepared in accordance with ASTM D2657, ASTM F 2389 and the manufacturer’s specifications.

  - Joint preparation, setting and alignment, fusion process, cooling times and working pressure shall be in accordance with the pipe and fitting manufacturer’s specifications.

E.	       Data Loggers shall be used to log each joint made. Data logger shall record at       least the date, time of day and person making each joint. Data logger shall also record the required pressure/leak test for manufacturer’s warranty.

- POLYPROPYLENE VALVES AND VALVE APPLICATIONS

  - Polypropylene Valves shall be manufactured in accordance with the manufacturer’s specifications and shall comply with the performance requirements of ASTM F 2389 or CSA B137.11.  The valves shall contain no rework or recycled thermoplastic materials except that generated in the manufacturer's own plant from resin of the same specification from the same raw material.

  - Valves shall be Aquatherm® Green pipe® available from Aquatherm, NA.  Valve specifications and ordering information are available at www.aquatherm.com.

- Install gate valves close to the main on each branch and riser serving two or more plumbing fixtures or equipment connections and where indicated.

- Install gate or ball valves on the inlet to each plumbing equipment item, on each supply to each plumbing fixture not having stops on supplies, and elsewhere as indicated.

- Install drain valves at the base of each riser, at low points of horizontal runs, and where required to drain the water distribution piping system.

- Install swing check valves on the discharge side of each pump and elsewhere as indicated.

- Install ball valves in each hot-water circulating loop and on the discharge side of each pump.

  - PIPING INSTALLATIONS

- Fire stopping shall be provided to both be compatible with the Aquatherm Piping and meet the requirements of ASTM E 814 or ULC S115 , “Fire Tests of Through-Penetration Firestops”.  Pipe insulations or fire resistive coating shall be removed where the pipe passes through a fire stop and, if required by the firestop manufacturer, for 3 inches beyond the firestop outside of the fire barrier.

- When installed in systems with pumps in excess of 3.0 HP, piping shall be protected from excessive heat generated by operating the pump at shut-off conditions.  Where the possibility exists that the pump will operate with no flow, the protection method shall be a temperature relief valve or comparable level of protection, set to a maximum temperature of 185°F.

- Aquatherm polypropylene PP-R can absorb small vibrations, so isolators are not required if the pipe (pipe diameters 4” and less) has some limited mobility on either side of the pump or equipment to which it is connected. For pipe sizes 6” and above provide vibration isolation couplings or connectors at pipe/pump connections.

- If heat tracing is specified for the piping, it should be installed on the pipe interior or exterior. It must be suitable for use with plastic piping and be self-regulating to ensure the surface temperature of the pipe and fittings will not exceed 158°F (70°C).

- Threaded Transition Joints: Join pipe fittings and valves as follows:

    - Apply appropriate tape or thread compound to external pipe threads.

    - Damaged Threads: Do not use pipe or pipe fittings with threads that are corroded or damaged.

    - Do NOT thread polypropylene pipe. Use threaded transition fitting.

3.6	HANGER AND SUPPORT INSTALLATION

Retain first paragraph below if Project is in a seismic area.

Comply with requirements for seismic-restraint devices in Section XXXXXX "Vibration and Seismic Controls for Plumbing Piping and Equipment."

Comply with requirements for pipe hanger, support products, and installation in Section XXXXXX "Hangers and Supports for Plumbing Piping and Equipment."

Vertical Piping:  MSS Type 8 or 42, clamps.

Individual, Straight, Horizontal Piping Runs:

Adjustable, steel clevis hangers.

Clamps on strut trapeze.

Clamps on strut attached to structure.

Clamps attached directly to the structure.

Base of Vertical Piping:  MSS Type 52, spring hangers.

Support vertical piping and tubing at base and at each floor. For piping 2” (63mm) or smaller, install mid-story guides.

Install hangers and supports at intervals specified in the applicable Plumbing Code and/or as recommended by pipe manufacturer.

Hangers and supports shall also be provided within 1-foot of every change of direction and within 1-foot of any pipe fittings and valves.

For hot water piping, provide clamps and supports that are felt or rubber/vinyl coated or lined.

For cold water piping supports and clamps may be bare metal. Ensure that the clamp or support does not have sharp edges that may scrape or gouge the piping.

Use care when installing riser clamps to not over tighten the clamps to cause indentation of the pipe. Riser clamps shall be isolated from the building structure by placing felt or rubber pads between the clamp and the structure.

All piping support materials shall be new and manufactured for the specific purpose of supporting systems, equipment, pipes and accessories. No improvised pipe support solutions shall be allowed.

Piping systems shall not have direct contact with the building structure. Provide isolation at tub and shower valves and pipes passing through studs, joists or plates. Use iron pipe sizes to fit Aquatherm pipe. Acceptable manufacturers for pipe/structure isolation:

- Holdrite

- Oatey

- Sioux Chief

- Walraven

3.7	EXPANSION AND CONTRACTION

- Provide expansion and contraction controls, guides and anchors to take into account the expansion and contraction of the pipe. Provide expansion loops or offsets as required and as indicated in the Aquatherm Design Guide.

While Aquatherm MF (faser) piping can absorb most of their own expansion stresses, this can cause the pipe to bow or bend.

Install anchor points at least every 120 feet.

Install expansion loop or offset between each anchor point. Expansion device must be able to absorb all of the stresses between the two anchor points. Refer to manufacturer’s published instructions, formulas and calculations at www.aquatherm.com.

Non-MF pipes used for hot applications shall have expansion controls every 30 feet of straight runs.

Vertical risers of MF piping shall be anchored at each floor. Piping 2” and smaller shall have mid-story guides installed to prevent bowing.

Provide anchor point at branch take-off in vertical riser of MF piping.

3.8 	PRESSURE/LEAK TESTING

- While still accessible all piping shall be pressure/leak tested to the   manufacturer’s standards.

- Tests shall be carried out using water, compressed air or a mixture of the two. The test pressure shall be as indicated in the pressure leak testing procedures required by the manufacturer.

- Any leaks detected shall be repaired at the contractor’s expense by removing the leaking part and replacing with new parts welded per the pipe manufacturer’s guidelines. Retest piping or portion thereof until satisfactory results are obtained. See www.aquatherm.com for additional details and forms.

- In the event that water is not available for testing it shall be permissible to use compressed air as a testing medium. Contact the engineering department of the manufacturer for guidance. Follow all precautionary procedures recommended by the piping manufacturer.

- Prepare reports for tests and submit to www.Aquatherm.com to obtain warranty.

3.9       CLEANING AND DISINFECTION

- Do not enclose, cover, or put piping into operation until it has been inspected and approved by authorities having jurisdiction.

- The pipes shall be flushed with cold water after finishing the installation. Flush the system until the water runs clear of debris and dirt.

- Clean, flush and disinfect potable water piping system following the guidelines of Aquatherm technical bulletin 201702A-AQTTB - Flushing Aquatherm Piping Systems

- Inspect and test piping systems following procedures of authorities having jurisdiction and as specified by the piping system manufacturer.

3.10      ADJUSTING

- Perform the following adjustments before operation:

- Close drain valves, hydrants, and hose bibbs.

- Open shutoff valves to fully open position.

- Open throttling valves to proper setting.

- Adjust balancing valves in hot-water-circulation return piping to provide adequate flow.

Manually adjust ball-type balancing valves in hot-water-circulation return piping to provide hot-water flow in each branch.

Adjust calibrated balancing valves to flows indicated.

- Remove plugs used during testing of piping and for temporary sealing of piping during installation.

6. Remove and clean strainer screens. Close drain valves and replace drain plugs.

7. Remove filter cartridges from housings and verify that cartridges are as specified for application where used and are clean and ready for use.

8.  Check plumbing specialties and verify proper settings, adjustments, and operation.

3.11        AQUATHERM MAINTENANCE PLAN

- Aquatherm pipe is pretty much “maintenance free” as an installation goes, but there are a few things that need to be observed after installation of the product. Adhering to these points will ensure a long and happy life with Aquatherm pipe.

- The design and installation of the Aquatherm piping was carried out with anticipated temperatures and pressures. The piping chosen for the project was chosen based on these parameters. If the temperature or pressure of this Aquatherm piping system is required to change, please notify Aquatherm Engineering (engineering@aquatherm.com or call (801)805-6657) to ensure that the proposed changes are within the limits of the installed piping.

- The design and installation of the Aquatherm piping was carried out with the anticipation that certain chemicals would be in the water or chemicals themselves would be carried directly by the piping. The piping chosen for the project was chosen based on these parameters. If the chemistry of the water or chemical carried by this Aquatherm piping system is required to change, please notify Aquatherm Engineering (engineering@aquatherm.com or call (801)805-6657) to ensure that the proposed changes are within the limits of the installed piping.

- Aquatherm pipe, copper pipe and domestic hot chlorinated water mixed together in a recirculating system can cause problems. Please note the following parameters if copper piping is to be introduced into the Aquatherm piping system. Please refer to: 201207C – AQTTB - Integration of other systems or components with Aquatherm piping for pressure pipe applications.

- Do not mix Aquatherm pipe with other piping systems in conditions that will cause the other system or components to fail.

- The temperature of the system must not exceed 140oF

- The velocity of the system must be maintained at 3 ft./sec. or slower.

- Small amounts of copper or brass in valves and other equipment will generally not cause an issue.

- Hydraulically balance a DHWR-system and ensure the required flow rate for each area of the building

- Do not add additional chlorine, chloramine, chlorine dioxide, on-site copper ion generation or other disinfectants to the DHWR system without first consulting with Aquatherm’s Engineering Department in Lindon Utah at (801)642-4145 or engineering@aquatherm.com

- The above guidelines do not apply to hydronic heating systems.

- If there are flanged connections or butterfly valve connections in the Aquatherm system, please follow the guidelines noted in our technical bulletin 201405B – AQTTB – Flanges and Butterfly Installation Guidelines. Please note that flange bolts and nuts can loosen over time from expansion and contraction and may need to be periodically re-tightened. It is wise to check these connections on a regular basis to ensure that loosening has not occurred.

- Aquatherm valves are popular valves to use in Aquatherm systems. The following maintenance guidelines need to be observed.

- The valve manufacturer recommends that the valve be cleaned periodically depending on external conditions.

- Clean only with a damp cloth. Do not use chemicals that will corrode the housing or the seals.

- The valve should be checked for functionality (exercised) at least quarterly. The following are suggestions for checking the valve for functionality.

        - Verify the direction for turning the valve.

        - Verify that the valve is installed correctly. See Aquatherm Technical Bulletin No.201609A – AQTTB – Aquatherm Polypropylene Valve Installation Notes

        - Close the valve slowly.

        - Open the valve slowly

        - Repeat the open/close cycle at least three (3) times

- It is recommended that the customer add the Aquatherm piping system and piping equipment into their structured Facility Inspection and Equipment Maintenance Plans

END OF SECTION

Revisions

12 Dec 2019 – Added Aquatherm Maintenance Plan

22 April 2020 – Added Molded fittings to UV protection

- Added Training requirement to Warranty section

12 April 2021 – Added Delivery, Handling and Storage Section

12 June 2021 – Coordinated with MasterSpec section

28 December 2021 - Added Performance Requirements Section,

- Added Warranty for pre-fab items

- Added data logger requirement

- Added compressed air for testing where water is not available