22 70 00 STORM DRAINAGE, RECLAIMED OR RECYCLED WATER PIPING

PART 1 – GENERAL

  - SUMMARY

- This Section specifies the reclaimed or recycled water piping system, including associated fittings, and specialties within the building.

  - RELATED SECTIONS

- Drawings and general provisions of the Contract, including General and Supplementary Conditions, Section XXXXXX and Division 1 Specification sections apply to work of this section.

  - REFERENCE DOCUMENTS

- ASTM F 2389-07 - Standard Specification for Pressure-rated Polypropylene (PP) Piping Systems

- CSA B137.11 - Polypropylene (PP-R) Pipe and Fittings for Pressure Applications

- NSF/ANSI 14 – Plastic Piping System Components and Related Materials

  - DEFINITIONS

- Definitions shall be in accordance with local plumbing and mechanical codes and ASTM F 2389.

  - SUBMITTALS

A. 	Material list naming each product to be used identified by manufacturer and product number, in accordance with Section 01 30 00.

  - QUALITY ASSURANCE

- Material shall be certified by NSF International as complying with NSF 14, and ASTM F 2389 or CSA B137.11.

- Material shall comply with manufacturers specifications.

- Special Engineered products shall be certified by NSF International as complying with NSF 14.

PART 2 – PRODUCTS

2.01 PIPE AND PIPING PRODUCTS

A. 	Pipe shall be manufactured from a PP-R resin (Fusiolen) meeting the short-term properties and long-term strength requirements of ASTM F 2389 or CSA B137.11. The pipe shall contain no rework or recycled materials except that generated in the manufacturer's own plant from resin of the same specification from the same raw material.  All pipe shall comply with the rated pressure requirements of ASTM F 2389 or CSA B137.11.  All pipe shall be certified by NSF International as complying with NSF 14, and ASTM F 2389 or CSA B137.11.

B. 	Pipe shall be Aquatherm® Lilac® available from Aquatherm, NA.  Piping specifications and ordering information are available at www.aquatherm.com.

2.02 FITTINGS

A.	Fittings shall be manufactured from a PP-R resin (Fusiolen) meeting the short-term properties and long-term strength requirements of ASTM F 2389.  The fittings shall contain no rework or recycled materials except that generated in the manufacturer's own plant from resin of the same specification from the same raw material.  All fittings shall be certified by NSF International as complying with NSF 14, and ASTM F 2389 or CSA B137.11.

B. 	Fittings shall be Aquatherm® Green pipe® available from Aquatherm, NA.  Fittings specifications and ordering information are available at www.aquatherm.com.

2.03 WARRANTY

A.	Manufacturer shall warrant pipe and fittings for 10 years to be free of defects in materials or manufacturing.

- Warranty shall cover labor and material costs of repairing and/or replacing defective materials and repairing any incidental damage caused by failure of the piping system due to defects in materials or manufacturing.

- Warranty shall be in effect only upon submission by the contractor to the manufacturer valid pressure/leak test documentation indicating that the system was tested and passed the manufacturer’s pressure/leak test.

2.04 VALVES

A.	Valves shall be manufactured in accordance with the manufacturer’s specifications and shall comply with the performance requirements of ASTM F 2389 or CSA B137.11.  The valves shall contain no rework or recycled thermoplastic materials except that generated in the manufacturer's own plant from resin of the same specification from the same raw material.

B. 	Valves shall be Aquatherm® Green pipe® available from Aquatherm, NA.  Valve specifications and ordering information are available at www.aquatherm.com.

2.05 SMOKE AND FIRE RATINGS

A.  Where indicated on the drawings that a Plenum-rated Piping System is needed, the pipe shall be wrapped and/or insulated with standard pipe insulation, field installed.  The pipe wrap or insulation shall meet the requirements of CAN/ULC-S102.2-03 or ASTM E84. The system shall have a Flame Spread Classification of less than 25 and Smoke Development rating of less than 50.

2.06 UV PROTECTION

A.  Where indicated on the drawings that the pipe will be exposed to direct UV light for more than 30 days, it shall be provided with a Factory applied, UV-resistant coating or alternative UV protection.

2.07 THERMAL AND VAPOR BARRIER

- Insulation materials furnished and installed hereunder should meet the minimum thickness requirements of American Society of Heating, Refrigeration, and Air Conditioning Engineers ASHRAE 90.1 (current edition), "Energy Efficient Design of New Buildings."  However, if other factors such as condensation control or personnel protection are to be considered, the selection of the thickness of insulation should satisfy the controlling factor.

- Where standard pipe insulation is indicated on the drawings or in these specifications, the contractor shall provide a thermal (radiant, conductive, and convective) and vapor barrier insulation. The insulation products shall be provided in ______ R-value and _____thickness or as indicated on the drawings or elsewhere in these specifications. The standard pipe insulation shall be UV resistant, CFC-free, non-porous, non-fibrous, and resist mold growth.

- For indoor systems operating at temperatures from 0°F (-18°C) to 200°F (93°C):

- Owens CorningTM FiberglasTM Insulation for Aquatherm with SSL II® Positive Closure System, or approved equal.

- For systems operating below ambient (32°F (0°C) to +65°F (18°C)) temperature:

- Owens CorningTM VaporWick® Pipe Insulation for Aquatherm, or approved equal.

2.08 COLOR AND MARKING OF PIPE

- All reclaimed water, recycled water, and gray water pipe shall be marked with “CAUTION: NONPOTABLE RECYCLED / RECLAIMED WATER, DO NOT DRINK” at intervals not to exceed three feet.

- All reclaimed water, recycled water, and gray water pipe shall be manufactured with purple color integral to the pipe

PART 3 - EXECUTION

- PIPING APPLICATIONS

  - Drawing plans, schematics, and diagrams indicate general location and arrangement of domestic water piping.  Indicated locations and arrangements are used to size pipe and calculate friction loss, expansion, and other design considerations.  Install piping as indicated unless deviations to layout are approved on coordination drawings.

  - Installers shall be trained and certified to install the pipe according to the manufacturer’s guidelines. Contact your local Aquatherm representative for training.

  - Install listed pipe materials and joining methods in the following applications:

    - Non-potable water pressurized systems used for irrigation:  Polypropylene (PP-R) piping in SDR 7.4 for sizes ½-inch and ¾-inch, and SDR 11 for sizes 1-inch through 10-inch.

    - Non-potable water pressurized systems used for domestic cold-water supply:  Polypropylene (PP-R) piping in SDR 7.4 for sizes ½-inch and ¾-inch, and SDR 11 for sizes 1-inch through 10-inch.

    - Non-potable water pressurized systems used for rainwater catchment:  Polypropylene (PP-R) piping in SDR 7.4 for sizes ½-inch and ¾-inch, and SDR 11 for sizes 1-inch through 10-inch.

    - Other non-potable water (gray water, reclaimed water, recycled water) systems with operating pressures at or below the rated pressure of the Aquatherm® lilac® piping system.

  - Installation must be accomplished with the proper tools for installing Aquatherm piping following manufacturer’s instructions. Installation tools are available from your local Aquatherm representative. Tools may be purchased or rented.

  - Install domestic water piping level and plumb.

  - Install piping indicated to be exposed and piping in equipment rooms and service areas at right angles or parallel to building walls.  Diagonal runs are prohibited unless specifically indicated otherwise.

- FUSION WELDING OF JOINTS

  - Install fittings and joints using socket-fusion, elecrofusion, or butt-fusion as applicable for the fitting or joint type.  All fusion-weld joints shall be made in accordance with the pipe and fitting manufacturer’s specifications and product standards.

  - Fusion-weld tooling, welding machines, and electrofusion devices shall be as specified by the pipe and fittings manufacturer.

  - Prior to joining, the pipe and fittings shall be prepared in accordance with F 2389 and the manufacturer’s specifications.

  - Joint preparation, setting and alignment, fusion process, cooling times and working pressure shall be in accordance with the pipe and fitting manufacturer’s specifications.

- VALVE APPLICATIONS

  - Install gate valves close to the main on each branch and riser serving 2 or more equipment connections and where indicated.

  - Install gate or ball valves on the inlet to each equipment item and elsewhere as indicated.

  - Install drain valve at the base of each riser, at low points of horizontal runs, and where required to drain hydronic piping system.

  - Install swing check valve on the discharge side of each pump and elsewhere as indicated.

  - Install ball valves in each hot-water circulating loop and the discharge side of each pump.

- PIPING INSTALLATIONS

  - Fire stopping shall be provided to both be compatible with the Aquatherm Piping and meet the requirements of ASTM E 814 or ULC S115 , “Fire Tests of Through-Penetration Firestops”.  Pipe insulations or fire resistive coating shall be removed where the pipe passes through a fire stop and, if required by the firestop manufacturer, for 3 inches beyond the firestop outside of the fire barrier.

  - When installed in systems with pumps in excess of 7.5 HP, piping shall be protected from excessive heat generated by operating the pump at shut-off conditions.  Where the possibility exists that the pump will operate with no flow, the protection method shall be a temperature relief valve or comparable level of protection, set to a maximum temperature of 185°F.

  - If heat tracing is specified for the piping, it should be installed on the pipe interior or exterior. It must be suitable for use with plastic piping and self-regulating to ensure the surface temperature of the pipe and fittings will not exceed 70°C (158°F).

3.5  HANGER AND SUPPORT INSTALLATION

Comply with requirements for seismic-restraint devices in Section XXXXXX "Vibration and Seismic Controls for Plumbing Piping and Equipment."

Comply with requirements for pipe hanger, support products, and installation in Section XXXXXX "Hangers and Supports for Plumbing Piping and Equipment."

Vertical Piping:  MSS Type 8 or 42, clamps.

Individual, Straight, Horizontal Piping Runs:

Adjustable, steel clevis hangers.

Clamps on strut trapeze.

Clamps on strut attached to structure.

Clamps attached directly to the structure.

Base of Vertical Piping:  MSS Type 52, spring hangers.

Support vertical piping and tubing at base and at each floor. For piping 2” (63mm) or smaller, install mid-story guides.

Install hangers and supports at intervals specified in the applicable Plumbing Code and/or as recommended by pipe manufacturer.

For hot water piping, provide clamps and supports that are felt or rubber/vinyl coated or lined.

For cold water piping supports and clamps may be bare metal. Ensure that the clamp or support does not have sharp edges that may scrape or gouge the piping.

Use care when installing riser clamps to not over tighten the clamps to cause indentation of the pipe.

3.6	EXPANSION AND CONTRACTION

- Provide expansion and contraction controls, guides and anchors to take into account the expansion and contraction of the pipe. Provide expansion loops or offsets as required and as indicated in the manufacturer’s literature.

While Aquatherm MF (faser) piping can absorb most of their own expansion stresses, this can cause the pipe to bow or bend.

Install anchor points at least every 120 feet.

Install expansion loop or offset between each anchor point. Expansion device must be able to absorb all of the stresses between the two anchor points. Refer to manufacturer’s published instructions, formulas and calculations at www.aquatherm.com.

Non-MF pipes used for hot applications shall have expansion controls every 30 feet of straight runs.

Vertical risers of MF piping shall be anchored at each floor.

Provide anchor point at branch take-off in vertical riser of MF piping.

3.7  	PRESSURE TESTING

A.  	While still accessible all piping shall be pressure/leak tested to the   manufacturer’s standards. Tests shall be carried out using water, compressed air or a mixture of the two. The test pressure shall be as indicated in the pressure leak testing procedures required by the manufacturer.  Any leaks detected shall be repaired at the contractor’s expense by removing the leaking part and replacing with new parts welded per the pipe manufacturer’s guidelines. See www.aquatherm.com for additional details and forms.

  - INSPECTING AND CLEANING

        - The pipes should be flushed with cold water after finishing the installation. Inspect and test piping systems following procedures of authorities having jurisdiction and as specified by the piping system manufacturer.

END OF SECTION