Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 232113.33 - GROUND-LOOP HEAT-PUMP PIPING

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section includes piping for [horizontal] [vertical], direct-buried, ground-loop, heat-pump systems.

ACTION SUBMITTALS

Product Data:  For each type of product.

Pipe and fittings.

Joining method and equipment.

Retain subparagraph below for climates and piping placement that require freeze protection.

Propylene glycol solution.

INFORMATIONAL SUBMITTALS

Field quality-control reports.

Borehole backfilling and drilling operations reports.

Dimensioned site layout.

Startup performance results.

PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products.  For an explanation of options and Contractor's product selection procedures, see Section 01600 "Product Requirements."

PIPES AND FITTINGS

Pipe shall be manufactured from a PP-R resin (Fusiolen) meeting the short-term properties and long-term strength requirements of ASTM F 2389.  The pipe shall contain no rework or recycled materials except that generated in the manufacturer's own plant from resin of the same specification from the same raw material.  All pipe shall be made in an extrusion process.  Domestic hot water shall contain a fiber layer (faser) to restrict thermal expansion. All pipe shall comply with the rated pressure requirements of ASTM F 2389.  All pipe shall be certified by NSF International as complying with NSF 14, NSF 61, and ASTM F 2389 or CSA B137.11.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.  Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

Pipe shall be Aquatherm® Green Pipe®, Green Pipe® MF (Faser®), Blue Pipe® MF® or Blue Pipe® MF® RCT® available from Aquatherm, NA.  Piping specifications and ordering information are available at www.aquatherm.com.See Evaluations for discussion on various pipe materials.

Fittings shall be manufactured from a PP-R resin (Fusiolen) meeting the short-term properties and long-term strength requirements of ASTM F 2389.  The fittings shall contain no rework or recycled materials except that generated in the manufacturer's own plant from resin of the same specification from the same raw material.  All fittings shall be certified by NSF International as complying with NSF 14, NSF 61, and ASTM F 2389 or CSA B137.11.

Fittings shall be Aquatherm® Green pipe® available from Aquatherm, NA.  Fittings specifications and ordering information are available at www.aquatherm.com.

U-Bend Assembly:  Factory fabricated with embossed depth stamp every [24 inches (600 mm)] [36 inches (900 mm)] <Insert dimension> from U-bend.

Revise pressure ratings in "Ground-Loop, Heat-Pump Piping Minimum Working Pressure" Paragraph below to suit Project.  Coordinate with Section 238146.13 "Water-to-Air Heat Pumps."

Ground-Loop, Heat-Pump Piping Minimum Working Pressure:  [160 psig (1100 kPa)] [200 psig (1380 kPa)] <Insert value>.

Ground-Loop, Heat-Pump Piping Operating Temperature:  Between 23 and 104 deg F (minus 5 and plus 40 deg C).

BOREHOLE BACKFILL

Retain this article only for boreholes.

Seal Material:  Bentonite clay with thermal conductivity greater than 1.07 Btu/h x sq. ft. x deg F (0.7 W/sq. m x K) according to ASTM D 5334.

Permeability:  Not more than 1 nm/s according to ASTM D 5084

ANTIFREEZE SOLUTION

Retain this article if piping is exposed to freezing temperatures.

Propylene Glycol:  Minimum 99 percent propylene glycol with corrosion inhibitors and environmental stabilizer additives to be mixed with water to protect piping circuit and connected equipment from physical damage caused by freezing or corrosion.

Quantity:  Sufficient solution for initial system startup and for preventive maintenance for one year from date of Substantial Completion.

Dilution Water:  Chloride content shall be less than 25 ppm, sulfate content less than 25 ppm, and hardness less than 100 ppm.

EXECUTION

EARTHWORK

Excavating, trenching, warning tape, and backfilling are specified in Section 312000 "Earth Moving."

HORIZONTAL PIPING INSTALLATION

Installers shall be trained and certified to install the pipe according to the manufacturer’s guidelines. Contact your local Aquatherm representative for training.

Separate trenches by 10 feet (3 m) minimum unless otherwise indicated.  Remove rocks in trenches that could contact pipe.

Backfill

Retain first paragraph below if installing pipe in body of water; otherwise, delete.

Extend pipe from trench onto bottom of body of water at an elevation that is at least 12 inches (300 mm) below frost line.  Seal membrane or impervious liner under body of water after installing piping.

Install PP-R piping in trenches according to ASTM D 2774 or ASTM F 645.

Clean PP-R pipe and fittings and make heat-fusion joints according to ASTM D 2657 and the manufacturer’s instructions.  Minimize number of joints.

Purge, flush, and pressure test piping before backfilling trenches.

Install continuous detectable warning tape for underground piping.  Locate tape a minimum of [24 inches (600 mm)] <Insert dimension> below finished grade, directly over piping.  Underground warning tapes are specified in Section 312000 "Earth Moving."

VERTICAL PIPING INSTALLATION

Retain this article if Project includes vertical piping in boreholes.

Install PP-R piping in boreholes according to ASTM D 2774 or ASTM F 645.

Installers shall be trained and certified to install the pipe according to the manufacturer’s guidelines. Contact your local Aquatherm representative for training.

Clean PP-R pipe and fittings and make heat-fusion joints according to ASTM D 2657 and manufacturer’s instructions.  Minimize number of joints.

Purge, flush, and pressure test piping before backfilling boreholes.

Completely fill the borehole from bottom to top with backfill material.

Install the header piping 4 to 6 inches (100 to 150 mm) deep and install the horizontal piping from the header to the boreholes.

Extend the horizontal piping and connect to ground-loop heat-pump piping systems at outside face of building wall in locations and pipe sizes indicated on the plans.

Terminate water-service piping at building wall until building ground-loop heat-pump piping systems are installed.  Terminate piping with caps.  Make connections to building ground-loop heat-pump piping systems when those systems are installed.

Backfill the horizontal piping and header trenches.

Fill the entire piping loop with water or antifreeze solution.

Maintain records of backfilling on-site.

Mark borehole locations, header pipes, and horizontal runs with metallic locator tape as specified in Section 230553 "Identification for HVAC Piping and Equipment."

Seal penetrations through building walls.

Wall sleeves are specified in Section 230517 "Sleeves and Sleeve Seals for HVAC Piping."

Mechanical sleeve seals are specified in Section 230517 "Sleeves and Sleeve Seals for HVAC Piping."

ANTIFREEZE SOLUTION FILL

Delete this article if using Section 232500 "HVAC Water Treatment."

Fill system with required quantity of propylene glycol and water to provide [minus 10 deg F (minus 23 deg C)] <Insert temperature> freezing temperature.

Test dilute solution using gas chromatography to verity concentration of propylene glycol, and forward report to Architect.

CONNECTIONS

Coordinate piping installations and specialty arrangements with Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

Drawings indicate general arrangement of piping, fittings, and specialties.

WARRANTY

Manufacturer shall warrant pipe and fittings for 10 years to be free of defects in materials or manufacturing.

Warranty shall cover labor and material costs of repairing and/or replacing defective materials and repairing any incidental damage caused by failure of the piping system due to defects in materials or manufacturing.

Warranty shall be in effect only upon submission by the contractor to the manufacturer of valid pressure/leak test documentation indicating that the system was tested and passed the manufacturer’s pressure/leak test.

FIELD QUALITY CONTROL

Piping Tests:  Fill piping 24 hours before testing and apply test pressure to stabilize piping.  Use potable water only.

Hydrostatic Tests:  Test at not less than 1-1/2 times the pipe working-pressure rating or 300 percent of system design pressure, whichever is more[, allowing for static pressure of borehole depth].

Increase pressure in 50-psig (345-kPa) increments and inspect each joint between increments.  Hold at test pressure for 30 minutes.  Slowly increase to next test pressure increment and hold for 30 minutes.  After testing at maximum test pressure, reduce pressure to 30 psig (207 kPa).  Hold for 90 minutes, and measure pressure at 30-minute intervals.  Repair leaks and retest until no leaks exist.

Maintain a minimum pipe velocity of 24 in./s (610 mm/s) for a minimum of 15 minutes to remove all air.

Test piping per manufacturer’s instructions to obtain warranty.

Prepare test and inspection reports. Submit reports to the architect and the manufacturer to obtain warranty.

END OF SECTION 232113.33