
Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 23 21 13.13 - UNDERGROUND HYDRONIC PIPING
Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

Note to Engineer: These specifications are minimum requirements and may be adjusted or added to by the engineer of record as he sees fit according to the project requirements.
1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. Plastic pipe and fittings.

2. Transition fittings.

3. Loose-fill insulation.

4. Cellular foam glass insulation

5. Pre-insulated piping

6. Data logging

1.3 PERFORMANCE REQUIREMENTS

A. Provide components and installation capable of producing hydronic piping systems with the following minimum working-pressure ratings:

Revise pressure ratings in three subparagraphs below.  Coordinate with Section 232113 "Hydronic Piping." Working pressure is equal to relief pressure plus the static height of the system and pumping head.  The only working pressure mandated by authorities having jurisdiction is for makeup water.

1. Hot-Water Piping:  [100 psig (690 kPa)] [150 psig (1035 kPa)] <Insert value> at [200 deg F (93 deg C)] <Insert temperature>.

2. Chilled-Water Piping:  [100 psig (690 kPa)] [150 psig (1035 kPa)] <Insert value> at [200 deg F (93 deg C)] <Insert temperature>.

3. Condenser-Water Piping:  [100 psig (690 kPa)] [150 psig (1035 kPa)] <Insert value> at [150 deg F (66 deg C)] <Insert temperature>.

1.4 REFERENCE DOCUMENTS

A. ASTM F 2389-07 - Standard Specification for Pressure-rated Polypropylene (PP) Piping Systems 

B. CSA B137.11 - Polypropylene (PP-R) Pipe and Fittings for Pressure Applications

C. NSF/ANSI 14 – Plastic Piping System Components and Related Materials
D. ASTM F1668 - Standard Guide for Construction Procedures for Buried Plastic Pipe

E. ASTM D2657 - Standard Practice for Heat Fusion Joining of Polyolefin Pipe and Fittings
F. DIN - DVS 2207-11 2017 - Welding thermoplastic materials - Heated element welding of pipes, piping parts and panels made of Polypropylene
1.5 ACTION SUBMITTALS

A. Product Data:  For the following:

1. Cellular Glass Insulation
2. Loose-fill insulation
3. Hydronic piping
4. Pre-insulated piping

B. LEED Submittals:

Retain subparagraph below if low-emitting materials are required for LEED Credit EQ 4.1; coordinate with requirements selected in Part 2 for adhesives.

1. Product Data for Credit EQ 4.1:  For adhesives, documentation including printed statement of VOC content and chemical components.

C. Shop Drawings:  For underground hydronic piping.  Signed and sealed by a professional engineer.

1. Show pipe sizes, locations, and elevations.  Show piping in trench, conduit, and cased pipe with details showing clearances between piping, and show insulation thickness.

1.6 INFORMATIONAL SUBMITTALS

Retain "Profile Drawings" Paragraph below if profiles are not shown on Drawings.

A. Profile Drawings:  Show system piping in elevation.  Draw profiles at horizontal scale of not less than 1-inch equals 50 feet (1:500) and at vertical scale of not less than 1-inch equals 5 feet (1:50).  Indicate manholes and piping.  Show types, sizes, materials, and elevations of other utilities crossing hydronic piping.

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as supplemented in "Quality Assurance" Article.

B. Qualification Data:  For qualified Installer.

Retain "Welding certificates" Paragraph below if retaining procedures for welder certification in "Quality Assurance" Article.

1.7 QUALITY ASSURANCE

Retain "Fiberglass Pipe and Fitting Installers" Paragraph below for fiberglass pipe assembly.

Retain "Welding Qualifications" Paragraph below if shop or field welding is required.  If retaining, also retain "Welding certificates" Paragraph in "Informational Submittals" Article.

A. Certify that each installer has been trained by the manufacturer’s representative for fusion piping installation.
PART 2 -  PRODUCTS

See "Writing Guide" Article in the Evaluations for a discussion of this Section's organization and the most efficient way to revise this Section.

2.1 PLASTIC PIPE AND FITTINGS

Retain this article for direct-bury piping or to describe materials for carrier pipe for conduit or cased piping.

See "Plastic Piping" Article in the Evaluations for discussion of product characteristics and maximum temperatures.

A. POLYPROPYLENE (PP-R) OR PP-RP(RCT) PIPE AND FITTINGS FOR WATER DISTRIBUTION AND WATER SERVICE

1. Pipe shall be manufactured from a PP-R or PP-RP(RCT) resin (Fusiolen) meeting the short-term properties and long-term strength requirements of ASTM F 2389.  The pipe shall contain no rework or recycled materials except that generated in the manufacturer's own plant from resin of the same specification from the same raw material.  All pipe shall be made in an extrusion process.  Domestic hot water piping shall contain a fiber layer (faser) to restrict thermal expansion. All pipe shall comply with the rated pressure requirements of ASTM F 2389.  All pipe shall be certified by NSF International as complying with NSF 14, NSF 61, and ASTM F 2389 or CSA B137.11.
2. Pipe shall be Aquatherm® Green Pipe®, Green Pipe® MF (Faser®), Blue Pipe® MF®, or Blue Pipe PP-RP(RCT)® available from Aquatherm, NA.  Piping specifications and ordering information are available at www.aquatherm.com.
3. Fittings shall be manufactured from a PP-R resin (Fusiolen) meeting the short-term properties and long-term strength requirements of ASTM F 2389.  The fittings shall contain no rework or recycled materials except that generated in the manufacturer's own plant from resin of the same specification from the same raw material.  All fittings shall be certified by NSF International as complying with NSF 14, NSF 61, and ASTM F 2389 or CSA B137.11.
4. Polypropylene Fittings: socket fusion, butt fusion, electrofusion, or fusion outlet fittings shall be used for fusion weld joints between pipe and fittings.  

5. Mechanical fittings and transition fittings shall be used where transitions are made to other piping materials or to valves and appurtenances.

6. Polypropylene pipe shall not be threaded.  Threaded brass or stainless steel transition fittings per ASTM F 2389 shall be used where a threaded connection is required.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.  Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Plastic, Pipe-Flange Gasket, Bolts, and Nuts:  Type and material recommended by piping system manufacturer unless otherwise indicated.

2.2 TRANSITION FITTINGS

A. Plastic-to-Metal Transition Fittings shall be the following:  
1. PP-R one-piece fitting with threaded stainless steel, brass, or copper insert and one PP-R fusion weld joint end.

2.3 DELIVERY STORAGE AND HANDLING

A. Inspect the pipe upon receipt to ensure that it has not been damaged during shipping.

B. Damaged pipe should be cataloged and returned for replacement following distributor’s procedures for returns.

C. Protect piping, valves, fittings, etc. before installation in accordance with manufacturer’s written instructions.

D. Always store the pipe on a flat surface. When storing the pipe on racks or supports on the ground always have at least four supports, evenly spaced, under a 19-ft length. Place plywood on top of the supports to prevent warping.

E. Piping shall be shipped from the factory with capped ends and stored on supports off the ground with ends covered at all times to prevent nesting of insects, birds, and other animals. Any pipe found to be without end-caps or not raised off of the ground should be cleaned by the contractor prior to installation.

F. Protect piping from accumulation of dirt and debris in and around piping/components.

G. If the pipe is removed from its bag, or the bag has been damaged do not store the pipe unprotected from UV rays (sunlight) for longer than six months. Pipe that is exposed to direct sunlight for longer than six months will not be covered under the warranty.

H. Never place the forks of a forklift into the ends of the pipe. The interior of the pipe may be damaged and can cause it to crack. Handlers may use a padded rug ram inside the pipe or use a crane or lift to handle larger pipe.

I. In cold weather, take extra care when handling the pipe. Cold temperatures reduce the pipe’s flexibility, making it more susceptible to impact damage.

2.4 WARRANTY

A. Manufacturer shall warrant pipe and fittings for 10 years to be free of defects in materials or manufacturing. 

B. Warranty shall cover labor and material costs of repairing and/or replacing defective materials and repairing any incidental damage caused by failure of the piping system due to defects in materials or manufacturing. 

C. Warranty shall be in effect only upon submission by the contractor to the manufacturer valid pressure/leak test documentation indicating that the system was tested and passed the manufacturer’s pressure/leak test. 

D. All Pre-Fab work performed by the manufacturer for the contractor shall be covered by the manufacturer’s 10-year warranty including welded joints and fittings.

E. Installers shall be trained and certified to install the pipe according to the manufacturer’s guidelines. Contact your local Aquatherm representative for training.

2.5 DIRECTIONAL BORING

A. Where required directional boring (horizontal directional drilling, HDD) also commonly referred to as guided horizontal boring may be utilized for the installation of the underground hydronic system. 
B. The work shall include all services, equipment, materials, and labor to complete the proper installation, testing, and restoration of underground utilities and environmental protection and restoration. 
C. The PP-R or PP-RP(RCT) pipe may be pulled in the directional boring application. Follow the recommendations provided by the manufacturer for maximum pull forces found in the manufacturer’s Design Guide. Do not apply more than the maximum safe pipe pull pressure at any time. 
D. The pulling head must be capable of matching the metric pipe. Pull heads may be constructed by the manufacturer or purchased from third party vendors such as Poly-Cam.  

E. Following successful pulling of the pipe, the pipe shall be pressure/leak tested per the requirements in this section.

F. Flush the pipe thoroughly and disinfect if required per the requirements of this section.
2.6 INSULATIONS

A. Granular Loose Fill Insulation
1. Granular, Loose-Fill Insulation:  Inorganic, nontoxic, nonflammable, sodium potassium aluminum silicate with calcium carbonate filler.  Include chemical treatment that renders insulation hydrophobic.

a. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:
b. Gilsulate International, Inc.

c. <Insert manufacturer's name>.

2. Thermal Conductivity (k-Value):  0.60 at 175 deg F (0.087 at 79 deg C) and 0.65 at 300 deg F (0.094 at 149 deg C).

3. Application Temperature Range:  35 to 800 deg F (2 to 426 deg C).

4. Dry Density:  40 to 42 lb/cu. ft. (640 to 672 kg/cu. m).

5. Strength:  12,000 lb/sq. ft. (58 600 kg/sq. m).

B. Powder, Loose-Fill Insulation:  Inert, nontoxic, nonflammable, calcium carbonate particles.  Include chemical treatment that renders insulation hydrophobic.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first subparagraph and list of manufacturers below.  See Section 016000 "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. DriTherm International Inc.

b. <Insert manufacturer's name>.

2. Thermal Conductivity (k-Value):  ASTM C 177, 0.58 at 100 deg F (0.084 at 37 deg C) and 0.68 at 300 deg F (0.098 at 149 deg C).

3. Application Temperature Range:  Minus 273 to plus 480 deg F (Minus 169 to plus 250 deg C).

4. Dry Density:  Approximately 60 lb/cu. ft. (960 kg/cu. m).

5. Strength:  12,000 lb/sq. ft. (58 600 kg/sq. m).

C. Cellular Glass Thermal Insulation: Cellular glass insulation, inert, non-toxic, impermeable, inorganic, noncombustible, cellular glass insulation. ASTM C 522-00
1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Pittsburgh Corning

b. <Insert manufacturer's name>.

2. Thermal Conductivity (k-Value):  ASTM C 177, 0.29 at 75 deg F (0.033 at 0 deg C).

3. Application Temperature Range:  Minus 273 to plus 900 deg F (Minus 169 to plus 482 deg C).

4. Dry Density:  Approximately 7.5 lb/cu. ft. (120 kg/cu. m).

5. Compressive Strength:  90 psi. (6.3 kg/sq. cm2).

D. Spray-on Pipe Insulation

1. Insulation shall be polyurethane foam or polyisocyanurate foam spray applied to the surface of the pipe with a minimum thickness of one inch. Insulation shall be rigid when dried, 90-95% closed cell polyurethane or polyisocyanurate with a 2.0 to 3.0 pounds per cubic foot density and coefficient of thermal conductivity (K- Factor) of 0.16 and shall conform to ASTM C-591. 
E. Pre-insulated Pipe

1. Pre-insulated pipe shall be a complete system of factory pre-insulated polypropylene piping for the specified service. 
2. Carrier pipe shall be polypropylene PP-R or PP-RP(RCT) by Aquatherm, conforming to ASTM F-2389 as previously specified herein. 
3. Insulation shall be polyurethane foam either spray applied or injected with one shot into the annular space between carrier pipe and jacket with a minimum thickness of one inch. Insulation shall be rigid, 90-95% closed cell polyurethane with a 2.0 to 3.0 pounds per cubic foot density and coefficient of thermal conductivity (K- Factor) of 0.16 and shall conform to ASTM C-591. 
4. Jacketing material shall be extruded, black, high-density polyethylene (HDPE), having a minimum wall thickness of 100 mils for jacket sizes less than or equal to 12”, and 125 mils for jacket sizes larger than 12” to 24”. 
5. Pre-insulated fittings (Tees and elbows) shall meet the same requirements as noted herein for pre-insulated pipe. Fittings shall have stubs of an extra 36” of pipe on each inlet and outlet for future ease of insertion into the piping system. Pre-insulator shall provide on-site insulation kit to connect to the pre-insulated system to make a continuous insulation system.
6. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Aquatherm TI Pipe

b. Insul-Tek Piping Systems, Inc.

c. Perma-Pipe, Inc.

d. Rovanco Piping Systems, Inc.

e. Thermacor Process, L.P.

f. Tricon Piping Systems, Inc.
g. <Insert manufacturer's name>.

PART 3 -  EXECUTION

3.1 EARTHWORK

A. See Section 312000 "Earth Moving" for excavating, trenching, and backfilling.

B. The pipe embedment materials shall be stable, sufficiently granular to be readily worked under the sides of the pipe to provide satisfactory haunching, and readily compactable to achieve soil densities specified by contract documents. These qualities are available in the following materials:

1. Gravels and sands classified as Soil Types GW, GP, SW, and SP, or by a dual soil classification beginning with one of these symbols, in accordance with Test Method D 2487.

2. Sands and gravels classified as Soil Types GM, GC, SM, and SC in accordance with Test Method D 2487.

C. Initial backfill materials shall be placed in compacted layers or as specified in contract documents and local codes.

D. All native and other materials in the pipe embedment zone shall be free from refuse, organic material, cobbles, boulders, large rocks or stones, or frozen soils.

E. The particle size of material in contact with the pipe shall not exceed the following: 

1. 1⁄2 in. for pipe to 4 in.

2. 3⁄4 in. for pipes 6 to 8 in. 

3. 1 in. for pipes 10 to 16 in.

4. 1-1⁄2 in. for larger pipes. 

5. Each soil layer shall be sufficiently compacted to uniformly develop lateral passive soil forces during the backfill operation.

F. The final backfill shall be placed and spread in approximately uniform layers in such a manner as to fill the trench completely so that there will be no unfilled spaces under or about rocks or lumps of earth in the backfill. Large rocks, stones, frozen clods, and other debris greater than 3 in. (76 mm) in diameter shall be removed. Hand mechanical compaction is the preferred method of compaction to a minimum of 12” of cover. When further compaction is required, rolling equipment or heavy tampers shall only be used to consolidate the final backfill, provided the pipe is covered by at least 18-in. of backfill. Initial backfill materials shall be placed in compacted layers of 6-in. A minimum of 12 to 18-in. of cover is required where light traffic is expected. A minimum cover of 24 in. shall be provided for locations with heavy traffic.
G. Trenches under pavements, sidewalks, or roads shall be backfilled and compacted to the required density specified by contract documents or by the appropriate government jurisdiction
3.2 PIPING APPLICATION

Retain at least one pipe material in paragraphs below for each service required for Project.  Services are specified separately to allow different pipe materials and joining methods for each.  If materials and methods are the same for all services, combine the requirements by revising the paragraph titles.  In general, pipe materials and joining methods in this article are as listed in the 2004 ASHRAE HANDBOOK - "HVAC Systems and Equipment," Ch. 41, "Pipes, Tubes, and Fittings."  The change point for pipe materials and joining methods is specified, in this master, where the pipe size changes from NPS 2 to NPS 2-1/2 (DN 50 to DN 65).  Revise this change point to suit office policy.  See "Writing Guide" Article in the Evaluations.

A. Hot-Water Heating Piping:

1. [NPS 2 (DN 50) and smaller] <Insert pipe size range> shall be [any of] the following:

Retain one or more of first four subparagraphs below.  If retaining more than one type of material and joining method and it is not the intent to give Contractor the option to select materials, delete the "any of" option in subparagraph above and identify each material on Drawings.  Show points of transition from one material to another.

a. Polypropylene (PP-R), (PP-RCT) ASTM F 2389, pipe and socket fusion, or fusion outlet fittings.

Retain "Loose-Fill Insulation" Subparagraph below to insulate bare underground piping.

b. Loose-Fill Insulation:  [Granular] [Powder].

c. Cellular Glass Thermal Insulation

d. Pre-insulated piping

2. [NPS 2-1/2 (DN 65) and larger] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of first four subparagraphs below.  If retaining more than one type of material and joining method and it is not the intent to give Contractor the option to select materials, delete the "any of" option in subparagraph above and identify each material on Drawings.  Show points of transition from one material to another.

a. Polypropylene (PP-R), (PP-RCT) ASTM F 2389, pipe and socket fusion, butt fusion, or fusion outlet fittings.

Retain "Loose-Fill Insulation" Subparagraph below to insulate bare underground piping.

b. Loose-Fill Insulation:  [Granular] [Powder].

c. Cellular Glass Thermal Insulation

d. Spray-on polyurethane/polyisocyanurate

e. Pre-insulated piping

Retain one of two subparagraphs below for factory-insulated underground piping.

B. Chilled-Water Piping:

1. [NPS 2 (DN 50) and smaller] <Insert pipe size range> shall be [ any of] the following:

Retain one or more of first four subparagraphs below.  If retaining more than one type of material and joining method and it is not the intent to give Contractor the option to select materials, delete the "any of" option in subparagraph above and identify each material on Drawings.  Show points of transition from one material to another.

a. Polypropylene (PP-R), (PP-RCT) ASTM F 2389, pipe and socket fusion, or fusion outlet fittings.

2. [NPS 2-1/2 (DN 65) and larger] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of first five subparagraphs below.  If retaining more than one type of material and joining method and it is not the intent to give Contractor the option to select materials, delete the "any of" option in subparagraph above and identify each material on Drawings.  Show points of transition from one material to another.

a. Polypropylene (PP-R), PP-RCT) ASTM F 2389, pipe and socket fusion, butt fusion, or fusion outlet fittings.

Retain "Loose-Fill Insulation" Subparagraph below to insulate bare underground piping.

Retain one of two subparagraphs below for factory-insulated underground piping.

C. Condenser-Water Piping:

1. [NPS 2 (DN 50) and smaller] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of first four subparagraphs below.  If retaining more than one type of material and joining method and it is not the intent to give Contractor the option to select materials, delete the "any of" option in subparagraph above and identify each material on Drawings.  Show points of transition from one material to another.

a. Polypropylene (PP-R), (PP-RCT) ASTM F 2389, pipe and socket fusion, or fusion outlet fittings.

2.  [NPS 2-1/2 (DN 65) and larger] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of first five subparagraphs below.  If retaining more than one type of material and joining method and it is not the intent to give Contractor the option to select materials, delete the "any of" option in subparagraph above and identify each material on Drawings.  Show points of transition from one material to another.

a. Polypropylene (PP-R), (PP-RCT) ASTM F 2389, pipe and socket fusion, butt fusion, or fusion outlet fittings.

Retain one of two subparagraphs below for factory-insulated underground piping.

3.3 PIPING INSTALLATION

A. Drawing plans, schematics, and diagrams indicate general location and arrangement of piping systems.  Indicate piping locations and arrangements if such were used to size pipe and calculate friction loss, expansion, pump sizing, and other design considerations.  Install piping as indicated unless deviations to layout are approved on Coordination Drawings.

B. Installers shall be trained and certified to install the pipe per the manufacturer’s guidelines. Contact your local Aquatherm representative for training.
C. Remove standing water in the bottom of trench.

D. Do not backfill piping trench until field quality-control testing has been completed and results approved.

E. Install piping at uniform grade of 0.2 percent.  Install drains, consisting of a tee fitting, NPS 3/4 (DN 20) ball valve, and short NPS 3/4 (DN 20) threaded nipple with cap, at low points and elsewhere as required for system drainage.  Install manual air vents at high points.

F. In conduits, install drain valves at low points and manual air vents at high points.

G. Install components with pressure rating equal to or greater than system operating pressure.

H. Install piping free of sags and bends.

I. Install fittings for changes in direction and branch connections.

J. See Section 230517 "Sleeves and Sleeve Seals for HVAC Piping" for sleeves and mechanical sleeve seals through exterior building walls.

K. Thrust blocks shall not be required with PP-R or PP-RP (RCT) piping.
L. Expansion loops shall not be required for direct buried underground PP-R or PP-RP(RCT) piping.

3.4 LOOSE-FILL INSULATION INSTALLATION

Retain this article for bare pipe installation requiring insulation.

A. Do not disturb the bottom of trench; otherwise, compact and stabilize it to ensure proper support.

B. Remove standing water in the bottom of trench.

C. Bed the pipe on a minimum 6-inch (150-mm) layer of granular fill material with a minimum 6-inch (150-mm) clearance between the pipes.

D. Form insulation trench by excavation or by installing drywall side forms to establish required height and width of the insulation.

E. Support piping with proper pitch, separation, and clearance to backfill or side forms using temporary supporting devices that can be removed after back filling with insulation.

F. Place insulation and backfill after field quality-control testing has been completed and results approved.

G. Pour loose-fill insulation to required dimension agitating insulation to eliminate voids around piping.

H. Remove temporary hangers and supports.

I. Cover loose-fill insulation with polyethylene sheet a minimum of 4 mils (0.10 mm) thick, and empty loose-fill insulation bags on top.

J. Manually backfill 6 inches (150 mm) of clean backfill.  If mechanical compaction is required, manually backfill to 12 inches (300 mm) before using mechanical-compaction equipment.

3.5 
Cellular Glass Thermal Insulation INSTALLATION

K. Do not disturb the bottom of trench; otherwise, compact and stabilize it to ensure proper support.

L. Remove standing water in the bottom of trench.

M. Bed the pipe on a minimum 6-inch (150-mm) layer of granular fill material (sand) with a minimum 6-inch (150-mm) clearance between the pipes.

N. Insulation and jacketing shall be applied to the piping in 10’ segments (maximum) 

O. After completion, the segments are rotated 180o and the bottom of the jacketing and butt strips are inspected. Any defects or damage shall be replaced. With new insulation.

P. Jacketing and insulations joints shall be staggered.

Q. In larger diameter piping shorter segments can be insulated and jacketed if more practical.

R. Where conditions permit, insulation and jacketing may be applied outside of the trench to sections of piping. Pipe lengths should be insulated in segments. Length of insulation segment should not exceed 10' (3 m).

S. Backfill per manufacturer’s instructions.

3.6 JOINT CONSTRUCTION

A. See Section 330500 "Common Work Results for Utilities" for basic piping joint construction.

B. Ream ends of pipes and tubes and remove burrs.  
C. Remove scale, slag, dirt, and debris from inside and outside of pipe and fittings before assembly.

D. Fusion Joints: Fusion join polypropylene pipe in accordance with ASTM D2657, ASTM F 2389, and the manufacturer’s instructions.

E. Threaded Joints:  Thread pipe with tapered pipe threads according to ASME B1.20.1.   Join pipe fittings and valves as follows:

1. Apply appropriate tape or thread compound to external pipe threads unless dry seal threading is specified.

2. Damaged Threads:  Do not use pipe or pipe fittings with threads that are corroded or damaged.  Do not use pipe sections that have cracked or open welds.

F. Flanged Joints:  Select appropriate gasket material, size, type, and thickness for service application.  Install gasket concentrically positioned.  Use suitable lubricants on bolt threads.

G. Insulation joints made for pre-insulated pipe shall be done in accordance with the insulation manufacturer’s instructions.

H. Data loggers shall be used to log each joint made. Data logger shall record at least the date, time of day and person making the joint. Data logger shall also record the required pressure/leak test for Warranty. 

3.7 
PRESSURE TESTING

A. While still accessible all piping shall be pressure/leak tested to the   manufacturer’s standards. 

B. Tests shall be carried out using water, compressed air, or a mixture of the two. The  test procedure shall be as indicated in the pressure leak testing procedures required by the manufacturer. 

C. In the event that water is not available for testing it shall be permissible to use compressed air as a testing medium. Contact the engineering department of the manufacturer for guidance. Follow all precautionary procedures recommended by the piping manufacturer.  

D. Any leaks detected shall be repaired at the contractor’s expense by removing the leaking part and replacing with new parts welded per the pipe manufacturer’s guidelines. See www.aquatherm.com for additional details and forms.


3.8
INSPECTING AND CLEANING

A.
The pipes shall be flushed with cold water after finishing the installation. Flush the system until the water runs clear of debris and dirt. 

B. 
Inspect and test piping systems following procedures of authorities having jurisdiction and as      specified by the piping system manufacturer.

C. 
Clean and disinfect water distribution piping following procedures of the manufacturer and/or the authority having jurisdiction

3.9 
IDENTIFICATION

I. Install continuous metallic/plastic underground warning tapes during back filling of trenches for underground hydronic piping.  Locate tapes 6 to 8 inches (150 to 200 mm) below finished grade, directly over piping. Alternatively install 8 – 10 gage copper wire at 6” – 8” directly over the pipeline. Provide warning tapes above the wire at 6” to 8” below the finished grade directly over the pipeline. See Section 312000 "Earth Moving" for warning-tape materials and devices and their installation.

4.0 
FIELD QUALITY CONTROL

J. While still accessible all piping shall be pressure/leak tested to the   manufacturer’s standards. Tests shall be carried out using water, compressed air or a mixture of the two. The test pressure shall be as indicated in the pressure leak testing procedures required by the manufacturer.  Any leaks detected shall be repaired at the contractor’s expense by removing the leaking part and replacing with new parts welded per the pipe manufacturer’s guidelines. See www.aquatherm.com for additional details and forms
K. Prepare test and inspection reports. Deliver to Architect, owner and manufacturer to obtain product warranty
4.1 
AQUATHERM MAINTENANCE PLAN

A. Aquatherm pipe is pretty much “maintenance free” as an installation goes, but there are few things that need to be observed after installation of the product. Adhering to these points will ensure a long and happy life with Aquatherm pipe.

B. The design and installation of the Aquatherm piping was carried out with anticipated temperatures and pressures. The piping chosen for the project was chosen based on these parameters. If the temperature or pressure of this Aquatherm piping system is required to change, please notify Aquatherm Engineering (engineering@aquatherm.com or call (801)805-6657) to ensure that the proposed changes are within the limits of the installed piping.

C. The design and installation of the Aquatherm piping was carried out with the anticipation that certain chemicals would be in the water or chemicals themselves would be carried directly by the piping. The piping chosen for the project was chosen based on these parameters. If the chemistry of the water or chemical carried by this Aquatherm piping system is required to change, please notify Aquatherm Engineering (engineering@aquatherm.com or call (801)805-6657) to ensure that the proposed changes are within the limits of the installed piping.

D. 
Aquatherm pipe, copper pipe and domestic hot chlorinated water mixed together in a recirculating system can cause problems. Please note the following parameters if copper piping is to be introduced into the Aquatherm piping system. Please refer to: 201207C – AQTTB - Integration of other systems or components with Aquatherm piping for pressure pipe applications.

1. Do not mix Aquatherm pipe with other piping systems in conditions that will cause the other system or components to fail.

2. The temperature of the system must not exceed 140oF

3. The velocity of the system must be maintained at 3 ft./sec. or slower.

4. Small amounts of copper or brass in valves and other equipment will generally not cause an issue.

5. Hydraulically balance a DHWR-system and ensure the required flow rate for each area of the building

6. Do not add additional chlorine, chloramine, chlorine dioxide, on-site copper ion generation or other disinfectants to the DHWR system without first consulting with Aquatherm’s Engineering Department in Lindon Utah at (801)642-4145 or engineering@aquatherm.com

7. The above guidelines do not apply to hydronic heating systems.

     E. 
If there are flanged connections or butterfly valve connections in the Aquatherm system, please follow the guidelines noted in our technical bulletin 201405B – AQTTB – Flanges and Butterfly Installation Guidelines. Please note that flange bolts and nuts can loosen over time from expansion and contraction and may need to be periodically re-tightened. It is wise to check these connections on a regular basis to ensure that loosening has not occurred.

F. 
Aquatherm valves are popular valves to use in Aquatherm systems. The following maintenance guidelines need to be observed.


1. The valve manufacturer recommends that the valve be cleaned periodically depending on external conditions.

2. Clean only with a damp cloth. Do not use chemicals that will corrode the housing or the seals.

3. The valve should be checked for functionality (exercised) at least quarterly. The following are suggestions for checking the valve for functionality.



a. Verify the direction for turning the valve. 


b. Verify that the valve is installed correctly. See Aquatherm Technical Bulletin No.201609A – AQTTB – Aquatherm Polypropylene Valve Installation Notes



c. Close the valve slowly.



d. Open the valve slowly



e. Repeat the open/close cycle at least three (3) times

G. It is recommended that the customer add the Aquatherm piping system and piping equipment into their structured Facility Inspection and Equipment Maintenance Plans.
END OF SECTION 232113.13

Revisions:

4 Nov 2019 – Added PP-RP(RCT)
18 Nov 2021 – updated and revised

20 October 2022- Added Aquatherm Maintenance Plan
	UNDERGROUND HYDRONIC PIPING
	232113.13 - 8



